## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Network Waitaki Ltd
| Disclosure Date | 2026-08-31
| Disclosure Year (year ended) | 2026-03-31
Template for Schedule 10a
Prepared 2 June 2026.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Non-material) Amendment Determination 2026 [2026] NZCC 21.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012, as amended.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Network Waitaki Ltd
[15 empty] | For Year Ended | 2026-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | NJ792 | Scotts Bridge Rd | N/A | 413FED | 2025-04-01 | 45748.3681 | 2025-04-01 11:06 | 45748.4625 | 0.42013 | 0.0009592 | 13 | 5694 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms, Transformer and install new transformer and Tighten Line
10 |  | NJ793 | Haka Valley Rd | N/A | 413FED | 2025-04-02 | 45749.3812 | 2025-04-02 14:43 | 45749.6132 | 0.29573 | 0.00088541 | 12 | 4008 | Planned | 11.0 Planned Shutdown | Realign 11kV Line and Tightening work
11 |  | NJ795 | Milnes Rd | N/A | 413FED | 2025-04-03 | 45750.3625 | 2025-04-03 14:18 | 45750.5958 | 0.024792 | 7.3784e-05 | 1 | 336 | Planned | 11.0 Planned Shutdown | Replacing Pole & Transformer @ Pole 72381 and Reconfigure LV & 11kV Lines
12 |  | PR348 | Broken Hut Rd | N/A | 423FED | 2025-04-03 | 45750.3889 | 2025-04-03 12:54 | 45750.5375 | 0.17369 | 0.00081163 | 11 | 2354 | Planned | 11.0 Planned Shutdown | Tree Felling between Pole 875139 and 34699
13 |  | NJ794 | Home Creek Rd | N/A | 472FED | 2025-04-04 | 45751.3632 | 2025-04-04 11:33 | 45751.4812 | 0.062717 | 0.00036892 | 5 | 850 | Planned | 11.0 Planned Shutdown | Tightening 33kV/11kV Poles 37499, 37500, 38255,38261
14 |  | F5711 | 145 Cosey Dell | N/A | 479FED | 2025-04-05 | 45752.3597 | 2025-04-05 09:30 | 45752.3958 | 0.0038368 | 7.3784e-05 | 1 | 52 | Unplanned | 6.0 Wildlife | Rat Blew 11kV Link @ Pole 10335
15 |  | PR353 | Hayes Rd | N/A | 413FED | 2025-04-07 | 45754.3986 | 2025-04-07 14:00 | 45754.5833 | 0.2944 | 0.0011068 | 15 | 3990 | Planned | 11.0 Planned Shutdown | Felling Trees beween Pole 17280 and 71325
16 |  | PR357 | Glenn Settlement Rd | N/A | 422FED | 2025-04-09 | 45756.3965 | 2025-04-09 11:30 | 45756.4792 | 0.14927 | 0.0012543 | 17 | 2023 | Planned | 11.0 Planned Shutdown | Contractor Trimming Trees between Pole 12029-72555-18014
17 |  | PR351 | Special School Rd | N/A | 494FED | 2025-04-11 | 45758.3556 | 2025-04-11 13:36 | 45758.5667 | 0.87479 | 0.0028776 | 39 | 11856 | Planned | 11.0 Planned Shutdown | Replacing Pole 31915 and Transformer and Installing SFB
18 |  | F5714 | Burnside Rd | N/A | 451FED | 2025-04-13 | 45760.3618 | 2025-04-13 11:28 | 45760.4778 | 0.29248 | 0.0078949 | 107 | 3964 | Unplanned | 2.0 Vegetation | Bark From Trees Shorted Two 11kV Wires, causing them to drop to the ground @ Pole 39992
19 |  | PI212A | Ben Omar Rd | N/A | 424FED | 2025-04-15 | 45762.3403 | 2025-04-15 16:36 | 45762.6917 | 0.41068 | 0.00081163 | 11 | 5566 | Planned | 11.0 Planned Shutdown | Replacing Poles, Transformer, Tightening Poles
20 |  | NJ807 | Newlands Rd | N/A | 415FED | 2025-04-15 | 45762.3562 | 2025-04-15 14:00 | 45762.5833 | 0.19302 | 0.00059028 | 8 | 2616 | Planned | 11.0 Planned Shutdown | Replacing Poles 25614, 25642, 25643 and completing maintenance
21 |  | PR368 | Otiake Rd | N/A | 411FED | 2025-04-16 | 45763.3375 | 2025-04-16 16:12 | 45763.675 | 0.55265 | 0.0011806 | 16 | 7490 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 31864 and Pole 31867
22 |  | PI212B | Ben Omar Rd | N/A | 424FED | 2025-04-16 | 45763.3667 | 2025-04-16 10:47 | 45763.4493 | 0.096584 | 0.00081163 | 11 | 1309 | Planned | 11.0 Planned Shutdown | Replacing Poles, Transformer, Tightening Poles
23 |  | NJ808 | Springhill Rd | N/A | 428FED | 2025-04-17 | 45764.3562 | 2025-04-17 15:11 | 45764.6326 | 0.14683 | 0.00036892 | 5 | 1990 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms & Maintenance
24 |  | MB002 | Ferry Rd | N/A | 435FED | 2025-04-22 | 45769.3688 | 2025-04-22 15:00 | 45769.625 | 1.4158 | 0.0038368 | 52 | 19188 | Planned | 11.0 Planned Shutdown | Tightening 33kV & 11kV Lines
25 |  | MB003A | Hilderthorpe Rd | N/A | 455FED | 2025-04-23 | 45770.3757 | 2025-04-23 13:55 | 45770.5799 | 0.19523 | 0.00066406 | 9 | 2646 | Planned | 11.0 Planned Shutdown | Tightening 33kV & 11kV Lines
26 |  | MB003B | Hilderthorpe Rd | N/A | 455FED | 2025-04-24 | 45771.3757 | 2025-04-24 12:21 | 45771.5146 | 0.13281 | 0.00066406 | 9 | 1800 | Planned | 11.0 Planned Shutdown | Tightening 33kV & 11kV Lines
27 |  | F5505 | Special School Rd | N/A | 494FED | 2025-04-24 | 45771.5437 | 2025-04-24 14:11 | 45771.591 | 0.19568 | 0.0028776 | 39 | 2652 | Unplanned | 8.0 Defective Equipment | Replace Faulty Crossarm at Pole 31931
28 |  | F5774 | Settlement Rd | N/A | 411FED | 2025-04-28 | 45775.725 | 2025-04-28 19:15 | 45775.8021 | 0.065521 | 0.00059028 | 8 | 888 | Unplanned | 9.0 Cause Unknown | 2 DDOs Blown at Pole 27101
29 |  | MB007 | Smith Rd | N/A | 421FED | 2025-04-29 | 45776.3542 | 2025-04-29 15:14 | 45776.6347 | 0.53656 | 0.0013281 | 18 | 7272 | Planned | 11.0 Planned Shutdown | Replacing Crossarm & Poles
30 |  | MB009 | Kakanui Valley Rd | N/A | 415FED | 2025-04-29 | 45776.4042 | 2025-04-29 16:32 | 45776.6889 | 0.1396 | 0.00044271 | 6 | 1892 | Planned | 11.0 Planned Shutdown | Replace Pole 70570 and Transformer & install Transformer LV Fusing
31 |  | MB006 | Hall Rd | N/A | 415FED | 2025-05-02 | 45779.3562 | 2025-05-02 11:19 | 45779.4715 | 0.20822 | 0.0012543 | 17 | 2822 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms
32 |  | MB017 | Windsor | N/A | 449FED | 2025-05-07 | 45784.3583 | 2025-05-07 15:42 | 45784.6542 | 0.72294 | 0.001697 | 23 | 9798 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms
33 |  | MB010 | Haka Valley Rd | N/A | 413FED | 2025-05-08 | 45785.3549 | 2025-05-08 15:08 | 45785.6306 | 1.1131 | 0.0028038 | 38 | 15086 | Planned | 11.0 Planned Shutdown | Replace Poles and Tighening works
34 |  | MB018 | Victoria Hill Rd | N/A | 449FED | 2025-05-08 | 45785.3826 | 2025-05-08 14:48 | 45785.6167 | 0.39785 | 0.0011806 | 16 | 5392 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms
35 |  | F8442 | Burnside Rd | N/A | 451FED | 2025-05-08 | 45785.8528 | 2025-05-08 22:30 | 45785.9375 | 0.1956 | 0.0078949 | 107 | 2651 | Unplanned | 6.0 Wildlife | Swan flew into Lines near pole 39213
36 |  | MB011 | Haka Valley Rd | N/A | 413FED | 2025-05-09 | 45786.3576 | 2025-05-09 12:53 | 45786.5368 | 0.64724 | 0.0025087 | 34 | 8772 | Planned | 11.0 Planned Shutdown | Replace Poles and Tighening works
37 |  | F16414 | Kaura Hill Rd | N/A | 415FED | 2025-05-10 | 45787.3924 | 2025-05-10 10:27 | 45787.4354 | 0.27905 | 0.0045008 | 61 | 3782 | Unplanned | 8.0 Defective Equipment | Jumper off Pole 18599
38 |  | NJ818 | Airedale Rd | N/A | 429FED | 2025-05-13 | 45790.3792 | 2025-05-13 14:00 | 45790.5833 | 0.75924 | 0.0025825 | 35 | 10290 | Planned | 11.0 Planned Shutdown | Isolating & earthing power on 11kV Lines for Transpower to replace Structure
39 |  | NJ823 | Airedale Rd | N/A | 429FED | 2025-05-14 | 45791.359 | 2025-05-14 10:50 | 45791.4514 | 0.019627 | 0.00014757 | 2 | 266 | Planned | 11.0 Planned Shutdown | Isolating & earthing power on 11kV Lines for Transpower to replace Structure
40 |  | PR381 | Awamoa Rd | N/A | 416FED | 2025-05-15 | 45792.3632 | 2025-05-15 15:22 | 45792.6403 | 0.85376 | 0.0021397 | 29 | 11571 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
41 |  | NJ824 | Georgetown Pukeuri Rd | N/A | 456FED | 2025-05-15 | 45792.3757 | 2025-05-15 10:50 | 45792.4514 | 1.02 | 0.0035417 | 48 | 13824 | Planned | 11.0 Planned Shutdown | Isolating & earthing power on 11kV Lines for Transpower to replace Structure
42 |  | PR382 | Weston Ngapara Rd | N/A | 451FED | 2025-05-16 | 45793.3938 | 2025-05-16 12:41 | 45793.5285 | 0.14314 | 0.00073784 | 10 | 1940 | Planned | 11.0 Planned Shutdown | Replace Poile 19638
43 |  | NJ838 | Haka Valley Rd | N/A | 413FED | 2025-05-22 | 45799.4306 | 2025-05-22 11:03 | 45799.4604 | 0.0031727 | 7.3784e-05 | 1 | 43 | Planned | 11.0 Planned Shutdown | Replace Fuse Base in SFB
44 |  | PR404 | Haka Highway | N/A | 412FED | 2025-05-23 | 45800.5889 | 2025-05-23 16:23 | 45800.6826 | 0.57773 | 0.0042795 | 58 | 7830 | Planned | 11.0 Planned Shutdown | Tree Felling
45 |  | F5692 | 353 Awahomoko Rd | N/A | 464FED | 2025-05-26 | 45803.3 | 2025-05-26 09:30 | 45803.3958 | 0.010182 | 7.3784e-05 | 1 | 138 | Unplanned | 6.0 Wildlife | No Power - Rat
46 |  | PR396 | Ngapara-Georgetown Rd | N/A | 422FED | 2025-05-27 | 45804.3785 | 2025-05-27 14:11 | 45804.591 | 0.13547 | 0.00044271 | 6 | 1836 | Planned | 11.0 Planned Shutdown | Replace pole 75058 Replace RX with 15kVA
47 |  | PR397 | Ngapara-Georgetown Rd | N/A | 422FED | 2025-05-28 | 45805.3569 | 2025-05-28 14:38 | 45805.6097 | 0.13429 | 0.00036892 | 5 | 1820 | Planned | 11.0 Planned Shutdown | Replace Pole 72570, 72575 and Tx. Reconductor from Pole 41186 to 72575
48 |  | F5741 | 360 Corrigalls Rd | N/A | 413FED | 2025-05-29 | 45806.5938 | 2025-05-29 17:40 | 45806.7361 | 0.015126 | 7.3784e-05 | 1 | 205 | Unplanned | 9.0 Cause Unknown | No Power - Cause Unknown
49 |  | F10890-1 | Weston Ngapara Rd | N/A | 449FED | 2025-06-03 | 45811.0257 | 2025-06-03 01:21 | 45811.0563 | 0.0032465 | 7.3784e-05 | 1 | 44 | Unplanned | 9.0 Cause Unknown | No Power - Rats, AC fail to R686 Recloser
50 |  | F5698 | Kaura Hill Rd | N/A | 415FED | 2025-06-03 | 45811.3326 | 2025-06-03 08:35 | 45811.3576 | 0.21516 | 0.0059765 | 81 | 2916 | Unplanned | 9.0 Cause Unknown | Cause Unknown - Small Fire at Base of pole
51 |  | PR411 | Kaik Rd | N/A | 478FED | 2025-06-03 | 45811.375 | 2025-06-03 15:50 | 45811.6597 | 0.42352 | 0.001033 | 14 | 5740 | Planned | 11.0 Planned Shutdown | Replace Pole 71000 and Transformer
52 |  | PR412 | MacDonalds Rd | N/A | 455FED | 2025-06-04 | 45812.3729 | 2025-06-04 14:07 | 45812.5882 | 0.13724 | 0.00044271 | 6 | 1860 | Planned | 11.0 Planned Shutdown | Replacing T2931 with New TX 100KVA on pole 40022
53 |  | PR415 | Tokarahi Ngapara Rd | N/A | 421FED | 2025-06-05 | 45813.3694 | 2025-06-05 12:51 | 45813.5354 | 0.070538 | 0.00029514 | 4 | 956 | Planned | 11.0 Planned Shutdown | Replace Pole 38374
54 |  | PR417 | Joyce Rd | N/A | 480FED | 2025-06-06 | 45814.359 | 2025-06-06 13:38 | 45814.5681 | 0.31093 | 0.001033 | 14 | 4214 | Planned | 11.0 Planned Shutdown | Replace Pole 70133
55 |  | PR418 | Pig Island Rd | N/A | 449FED | 2025-06-10 | 45818.3542 | 2025-06-10 15:27 | 45818.6438 | 0.92238 | 0.0039106 | 53 | 12501 | Planned | 11.0 Planned Shutdown | Replace Poles
56 |  | PR420 | Kauru Hill Rd | N/A | 415FED | 2025-06-11 | 45819.3688 | 2025-06-11 14:05 | 45819.5868 | 0.39386 | 0.0012543 | 17 | 5338 | Planned | 11.0 Planned Shutdown | Replace Poles and maintenance
57 |  | NJ858 | Twizel Omarama Rd | N/A | 491FED | 2025-06-13 | 45821.3854 | 2025-06-13 12:59 | 45821.541 | 0.016528 | 7.3784e-05 | 1 | 224 | Planned | 11.0 Planned Shutdown | Install 11kV Links on pole 21176
58 |  | NJ860 | Broken Hut Rd | N/A | 423FED | 2025-06-17 | 45825.3542 | 2025-06-17 15:50 | 45825.6597 | 0.097395 | 0.00022135 | 3 | 1320 | Planned | 11.0 Planned Shutdown | Replace Pole 70793 and install new 30kva Tx
59 |  | NJ861 | Broken Hut Rd | N/A | 423FED | 2025-06-18 | 45826.3542 | 2025-06-18 15:53 | 45826.6618 | 0.32686 | 0.00073784 | 10 | 4430 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
60 |  | NJ863 | Ardgowan Rd | N/A | 430FED | 2025-06-18 | 45826.3861 | 2025-06-18 09:35 | 45826.3993 | 0.0028038 | 0.00014757 | 2 | 38 | Planned | 11.0 Planned Shutdown | Remove LV Conductor between poles 40322 & 40330 and appropriate hardware
61 |  | PR390 | Kurow Duntroon Rd | N/A | 411FED | 2025-06-18 | 45826.4097 | 2025-06-18 13:44 | 45826.5722 | 0.034531 | 0.00014757 | 2 | 468 | Planned | 11.0 Planned Shutdown | Replace pole 73886 replace stud pole 73887
62 |  | NJ862 | Broken Hut Rd | N/A | 423FED | 2025-06-19 | 45827.3688 | 2025-06-19 10:31 | 45827.4382 | 0.029514 | 0.00029514 | 4 | 400 | Planned | 11.0 Planned Shutdown | Replace 11kV Pole 71213
63 |  | F5613 | 1686 Weston Ngapara Rd | N/A | 420FED | 2025-06-20 | 45828.8576 | 2025-06-20 21:16 | 45828.8861 | 0.0030252 | 7.3784e-05 | 1 | 41 | Unplanned | 9.0 Cause Unknown | No Power - Blown DDOs
64 |  | PR439 | Tarbetness St | N/A | 417FED | 2025-06-23 | 45831.3583 | 2025-06-23 15:30 | 45831.6458 | 0.36656 | 0.00088541 | 12 | 4968 | Planned | 11.0 Planned Shutdown | Replacing Poles and Maintenance
65 |  | PR432 | Seacliff Rd | N/A | 478FED | 2025-06-26 | 45834.4201 | 2025-06-26 15:16 | 45834.6361 | 0.18358 | 0.00059028 | 8 | 2488 | Planned | 11.0 Planned Shutdown | Replace Termination - Pole 70279
66 |  | NJ886 | Taward St | N/A | 445FED | 2025-06-30 | 45838.4306 | 2025-06-30 12:31 | 45838.5215 | 0.019332 | 0.00014757 | 2 | 262 | Planned | 11.0 Planned Shutdown | Level Transformer TX3422.5
67 |  | NJ885 | Wallbrook Crescent | N/A | 438FED | 2025-07-09 | 45847.3854 | 2025-07-09 11:11 | 45847.466 | 0.20542 | 0.0017708 | 24 | 2784 | Planned | 11.0 Planned Shutdown | Install LV Monitor
68 |  | NJ902 | Charles St | N/A | 427FED | 2025-07-10 | 45848.3604 | 2025-07-10 15:38 | 45848.6514 | 0.49465 | 0.0011806 | 16 | 6704 | Planned | 11.0 Planned Shutdown | Replace Poles and Reconductoring
69 |  | PR458 | Battersby Rd | N/A | 449FED | 2025-07-15 | 45853.3431 | 2025-07-15 15:11 | 45853.6326 | 1.2923 | 0.0030989 | 42 | 17514 | Planned | 11.0 Planned Shutdown | Replace Poles and Arms
70 |  | NJ893 | Omarama-Otematata Rd | N/A | 423FED | 2025-07-16 | 45854.3542 | 2025-07-16 16:52 | 45854.7028 | 0.59264 | 0.0011806 | 16 | 8032 | Planned | 11.0 Planned Shutdown | Replace Pole 29648
71 |  | PR460 | McNalley Rd | N/A | 449FED | 2025-07-16 | 45854.3597 | 2025-07-16 22:31 | 45854.9382 | 0.083376 | 0.00073784 | 10 | 1130 | Planned | 11.0 Planned Shutdown | Install new Line DDOs to pole 39331
72 |  | PR461 | McNalley Rd | N/A | 449FED | 2025-07-16 | 45854.4437 | 2025-07-16 15:28 | 45854.6444 | 0.042647 | 0.00014757 | 2 | 578 | Planned | 11.0 Planned Shutdown | Install Transformer
73 |  | NJ894 | Omarama-Otematata Rd | N/A | 423FED | 2025-07-17 | 45855.3542 | 2025-07-17 12:49 | 45855.534 | 0.45864 | 0.0017708 | 24 | 6216 | Planned | 11.0 Planned Shutdown | Replace Poles and Arms
74 |  | NJ895 | Lindis | N/A | 423FED | 2025-07-18 | 45856.3576 | 2025-07-18 11:57 | 45856.4979 | 0.13414 | 0.00066406 | 9 | 1818 | Planned | 11.0 Planned Shutdown | Replace Poles
75 |  | NJ903 | Georgetown Pukeuri Rd | N/A | 221FED | 2025-07-21 | 45859.3993 | 2025-07-21 11:14 | 45859.4681 | 0.014609 | 0.00014757 | 2 | 198 | Planned | 11.0 Planned Shutdown | Replace LV Conductor
76 |  | NJ904 | Seven Mile Rd | N/A | 457FED | 2025-07-21 | 45859.4875 | 2025-07-21 13:34 | 45859.5653 | 0.0082639 | 7.3784e-05 | 1 | 112 | Planned | 11.0 Planned Shutdown | Replace LV Conductor
77 |  | PR462 | Prohibition Rd | N/A | 424FED | 2025-07-22 | 45860.3333 | 2025-07-22 13:08 | 45860.5472 | 0.4565 | 0.001697 | 23 | 6187 | Planned | 11.0 Planned Shutdown | Replace Poles
78 |  | F3935 | 919 Ngapara Georgetown Rd | N/A | 444FED | 2025-07-24 | 45862.3146 | 2025-07-24 09:14 | 45862.3847 | 0.0074522 | 7.3784e-05 | 1 | 101 | Unplanned | 8.0 Defective Equipment | No Power - Replace LV Fuse Base
79 |  | PR466 | Kaura Hill Rd | N/A | 415FED | 2025-07-25 | 45863.3347 | 2025-07-25 16:09 | 45863.6729 | 0.99011 | 0.0019922 | 27 | 13419 | Planned | 11.0 Planned Shutdown | Reconductoring
80 |  | F16361 | Tulliemet Rd | N/A | 479FED | 2025-07-25 | 45863.5813 | 2025-07-25 14:18 | 45863.5958 | 0.0030989 | 0.00014757 | 2 | 42 | Unplanned | 8.0 Defective Equipment | No Power - Replace LV Fuse Base
81 |  | F4453 | 1431 Glenavy-Hilderthorpe Rd | N/A | 478FED | 2025-07-28 | 45866.3187 | 2025-07-28 10:05 | 45866.4201 | 0.10773 | 0.00073784 | 10 | 1460 | Unplanned | 6.0 Wildlife | No Power - Blown DDOs, Swan
82 |  | PR467 | Kaura Hill Rd | N/A | 415FED | 2025-07-28 | 45866.3632 | 2025-07-28 16:35 | 45866.691 | 0.82078 | 0.0019922 | 27 | 11124 | Planned | 11.0 Planned Shutdown | Reconductoring
83 |  | PR468 | Kaura Hill Rd | N/A | 415FED | 2025-07-29 | 45867.359 | 2025-07-29 15:24 | 45867.6417 | 0.42042 | 0.001033 | 14 | 5698 | Planned | 11.0 Planned Shutdown | Reconductoring
84 |  | F16362 | 36 Finlays Rd | N/A | 420FED | 2025-07-29 | 45867.4792 | 2025-07-29 11:58 | 45867.4986 | 0.0061979 | 0.00022135 | 3 | 84 | Unplanned | 5.0 Third party Interference | Repair of SFB628191 - Hit by Truck
85 |  | F4624-1 | 5219 Kurow Duntroon Rd | N/A | 411FED | 2025-07-29 | 45867.7042 | 2025-07-29 18:21 | 45867.7646 | 0.0064192 | 7.3784e-05 | 1 | 87 | Unplanned | 5.0 Third party Interference | Blown DDOs -No Power - Potential Twig from Hedge Trimmer
86 |  | NJ918 | Omarama Ave | N/A | 423FED | 2025-07-30 | 45868.3611 | 2025-07-30 13:56 | 45868.5806 | 0.11658 | 0.00036892 | 5 | 1580 | Planned | 11.0 Planned Shutdown | Replace Pole 19038
87 |  | PR469 | Kaura Hill Rd | N/A | 415FED | 2025-07-30 | 45868.3639 | 2025-07-30 15:34 | 45868.6486 | 0.12101 | 0.00029514 | 4 | 1640 | Planned | 11.0 Planned Shutdown | Reconductoring
88 |  | PR470 | Kaura Hill Rd | N/A | 415FED | 2025-07-31 | 45869.359 | 2025-07-31 16:46 | 45869.6986 | 0.50513 | 0.001033 | 14 | 6846 | Planned | 11.0 Planned Shutdown | Reconductoring
89 |  | PR471 | Kaura Hill Rd | N/A | 415FED | 2025-08-01 | 45870.3569 | 2025-08-01 13:35 | 45870.566 | 0.91057 | 0.0030252 | 41 | 12341 | Planned | 11.0 Planned Shutdown | Reconductoring
90 |  | NJ923 | Eastern Rd | N/A | 494FED | 2025-08-01 | 45870.4653 | 2025-08-01 11:54 | 45870.4958 | 0.006493 | 0.00014757 | 2 | 88 | Planned | 11.0 Planned Shutdown | New Connection at Pole 870230
91 |  | F16366 | Kaura Hill Rd | N/A | 415FED | 2025-08-01 | 45870.5493 | 2025-08-01 14:33 | 45870.6062 | 0.0060503 | 7.3784e-05 | 1 | 82 | Planned | 11.0 Planned Shutdown | Install LV Monitor at Pole 72619
92 |  | NJ932 | 33/11kV Otematata Kurow Lines | N/A | 464FED | 2025-08-04 | 45873.4062 | 2025-08-04 14:46 | 45873.6153 | 0.33314 | 0.0011068 | 15 | 4515 | Planned | 11.0 Planned Shutdown | Tighten all hardware
93 |  | NJ934 | 33/11kV Otematata Kurow Lines | N/A | 464FED | 2025-08-06 | 45875.3806 | 2025-08-06 09:50 | 45875.4097 | 0.0061979 | 0.00014757 | 2 | 84 | Planned | 11.0 Planned Shutdown | Tighten all hardware
94 |  | PR477 | Happy Valley Rd | N/A | 416FED | 2025-08-07 | 45876.3333 | 2025-08-07 13:48 | 45876.575 | 0.17974 | 0.00051649 | 7 | 2436 | Planned | 11.0 Planned Shutdown | Tree Felling
95 |  | NJ938 | 33/11kV Otematata Kurow Lines | N/A | 464FED | 2025-08-08 | 45877.3569 | 2025-08-08 10:38 | 45877.4431 | 0.11946 | 0.0018446 | 25 | 1619 | Planned | 11.0 Planned Shutdown | Tighten all hardware
96 |  | PR480 | Pukeuri Oamaru Rd | N/A | 438FED | 2025-08-10 | 45879.3736 | 2025-08-10 16:23 | 45879.6826 | 0.13134 | 0.00029514 | 4 | 1780 | Planned | 11.0 Planned Shutdown | Replace 11kV cable shear links at Pole 70701 & 70704
97 |  | F6207 | 89 Brookstead Rd | N/A | 444FED | 2025-08-11 | 45880.6208 | 2025-08-11 15:53 | 45880.6618 | 0.0087066 | 0.00014757 | 2 | 118 | Unplanned | 5.0 Third party Interference | No Power - Blown HV Fuses - Possible Truck hoist hit
98 |  | F6259 | 404 Ferry Rd | N/A | 454FED | 2025-08-12 | 45881.2799 | 2025-08-12 08:17 | 45881.3451 | 0.0069357 | 7.3784e-05 | 1 | 94 | Unplanned | 6.0 Wildlife | No Power - Blown HV Fuses - Possum
99 |  | NJ943 | 11kV Line Falconers Rd | N/A | 479FED | 2025-08-12 | 45881.3549 | 2025-08-12 15:36 | 45881.65 | 0.7526 | 0.0017708 | 24 | 10200 | Planned | 11.0 Planned Shutdown | Replace Poles and Reconductoring
100 |  | F6315 | Eastern Rd | N/A | 496FED | 2025-08-12 | 45881.5437 | 2025-08-12 15:00 | 45881.625 | 0.0086328 | 7.3784e-05 | 1 | 117 | Unplanned | 9.0 Cause Unknown | No Power - Blown HV Fuses - Cause Unknown
101 |  | NJ943B | Falconers Rd | N/A | 479FED | 2025-08-13 | 45882.3549 | 2025-08-13 15:31 | 45882.6465 | 0.74375 | 0.0017708 | 24 | 10080 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms & Conductor
102 |  | NJ958 | Falconers Rd | N/A | 479FED | 2025-08-14 | 45883.3583 | 2025-08-14 13:23 | 45883.5576 | 0.10588 | 0.00036892 | 5 | 1435 | Planned | 11.0 Planned Shutdown | Replace Pole 30781 and Transformer and Replace Pole 30778 and Crossarms at Pole 30776
103 |  | PR482 | Fortification Rd | N/A | 428FED | 2025-08-15 | 45884.341 | 2025-08-15 14:59 | 45884.6243 | 0.18062 | 0.00044271 | 6 | 2448 | Planned | 11.0 Planned Shutdown | Replace Pole 43085 and Transformer
104 |  | NJ943C | Falconers Rd | N/A | 479FED | 2025-08-15 | 45884.3542 | 2025-08-15 13:19 | 45884.5549 | 0.51177 | 0.0017708 | 24 | 6936 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms & Conductor
105 |  | PI235 | 11kV Line Special School Rd | N/A | 494FED | 2025-08-15 | 45884.5424 | 2025-08-15 14:06 | 45884.5875 | 0.20143 | 0.0030989 | 42 | 2730 | Planned | 11.0 Planned Shutdown | Replace 11kV Crossarm @ Pole 31955
106 |  | PI236 | LV Line Special School Rd | N/A | 494FED | 2025-08-15 | 45884.6014 | 2025-08-15 15:47 | 45884.6576 | 0.011953 | 0.00014757 | 2 | 162 | Planned | 11.0 Planned Shutdown | Replace LV Service Crossarm @ Pole 31955
107 |  | JF003 | Hakataramea Valley Rd | N/A | 413FED | 2025-08-21 | 45890.3736 | 2025-08-21 16:23 | 45890.6826 | 0.10138 | 0.0013281 | 18 | 1374 | Planned | 11.0 Planned Shutdown | Tighten Pole 35564, 35563, 43033
108 |  | F7524 | Bluff Hill Rd | N/A | 479FED | 2025-08-23 | 45892.5118 | 2025-08-23 13:53 | 45892.5785 | 0.17 | 0.0017708 | 24 | 2304 | Unplanned | 8.0 Defective Equipment | 11kV Wire Down @ Pole 30031
109 |  | F813902 | Beach Rd | N/A | 408FED | 2025-08-24 | 45893.4458 | 2025-08-24 13:03 | 45893.5437 | 2.0304 | 0.09378 | 1271 | 27518 | Unplanned | 9.0 Cause Unknown | 11kV Jumpers Burnt off @ Pole 813902 and 39621
110 |  | 2981PI | Seven Mile Rd | N/A | 478FED | 2025-08-26 | 45895.3625 | 2025-08-26 14:58 | 45895.6236 | 0.29536 | 0.00073784 | 10 | 4003 | Planned | 11.0 Planned Shutdown | Trimming Trees with Machine
111 |  | PR485 | Shines Rd | N/A | 473FED | 2025-08-26 | 45895.3688 | 2025-08-26 14:22 | 45895.5986 | 0.14654 | 0.00044271 | 6 | 1986 | Planned | 11.0 Planned Shutdown | Replace Transformer at Pole 11842 and Replace LV Conductor between pole 11842-41269
112 |  | PR487 | Bushy Creek Rd | N/A | 421FED | 2025-08-27 | 45896.366 | 2025-08-27 14:03 | 45896.5854 | 0.32642 | 0.001033 | 14 | 4424 | Planned | 11.0 Planned Shutdown | Felling Trees Between Pole 43505 and 12801
113 |  | PR489 | Springhills Rd | N/A | 411FED | 2025-08-28 | 45897.366 | 2025-08-28 13:08 | 45897.5472 | 0.077031 | 0.00029514 | 4 | 1044 | Planned | 11.0 Planned Shutdown | Replacing Pole 40497 and 31829
114 |  | PR490 | Otiake Rd | N/A | 411FED | 2025-08-29 | 45898.3556 | 2025-08-29 15:10 | 45898.6319 | 0.96908 | 0.0024349 | 33 | 13134 | Planned | 11.0 Planned Shutdown | Replacing Crossarms and Tighening
115 |  | F8711 | 65 Hillgrove Moeraki Rd | N/A | 480FED | 2025-08-31 | 45900.7111 | 2025-08-31 22:35 | 45900.941 | 6.6714 | 0.024939 | 338 | 90418 | Unplanned | 5.0 Third party Interference | Car vs Pole 27546
116 |  | 16378 | College St | N/A | 458FED | 2025-09-04 | 45904.4257 | 2025-09-04 14:33 | 45904.6062 | 0.019184 | 7.3784e-05 | 1 | 260 | Unplanned | 8.0 Defective Equipment | Additional Switching to Release Request PR493 Operating Order 2994PI to Isolate 11kV Line College St
117 |  | NJ964 | Ngapara-Georgetown Rd | N/A | 422FED | 2025-09-09 | 45909.3764 | 2025-09-09 15:50 | 45909.6597 | 0.30104 | 0.00073784 | 10 | 4080 | Planned | 11.0 Planned Shutdown | Removing ABS1282 and Installing New Pole North of Pole 15951
118 |  | F16385 | Cnr Horse Gully Rd & Papakaio Hwy | N/A | 456FED | 2025-09-09 | 45909.7882 | 2025-09-09 21:31 | 45909.8965 | 0.20719 | 0.0013281 | 18 | 2808 | Unplanned | 5.0 Third party Interference | Tractor Broke Pole 23796
119 |  | PR495A | Broken Hut Rd | N/A | 423FED | 2025-09-10 | 45910.3549 | 2025-09-10 15:22 | 45910.6403 | 2.0015 | 0.0048698 | 66 | 27126 | Planned | 11.0 Planned Shutdown | Replace Poles and maintenance
120 |  | PR495B | Broken Hut Rd | N/A | 423FED | 2025-09-11 | 45911.3562 | 2025-09-11 13:45 | 45911.5729 | 1.5194 | 0.0048698 | 66 | 20592 | Planned | 11.0 Planned Shutdown | Replace Poles and maintenance
121 |  | F16387 | 62a Awamoa Rd | N/A | 408FED | 2025-09-15 | 45915.4201 | 2025-09-15 10:19 | 45915.4299 | 0.0041319 | 0.00029514 | 4 | 56 | Unplanned | 8.0 Defective Equipment | Replace Burnt up LV fuse base
122 |  | F10536 | 289 Fortification Rd | N/A | 416FED | 2025-09-15 | 45915.4271 | 2025-09-15 14:25 | 45915.6007 | 0.055338 | 0.00022135 | 3 | 750 | Unplanned | 9.0 Cause Unknown | Blown DDOs - Cause Unknown
123 |  | F16388 | SH1 Hilderthorpe | N/A | 478FED | 2025-09-15 | 45915.566 | 2025-09-15 17:02 | 45915.7097 | 0.36656 | 0.0017708 | 24 | 4968 | Unplanned | 5.0 Third party Interference | Car vs Pole 24229
124 |  | JF011 | McMullan Place | N/A | 436FED | 2025-09-16 | 45916.3938 | 2025-09-16 12:52 | 45916.5361 | 0.21176 | 0.001033 | 14 | 2870 | Planned | 11.0 Planned Shutdown | Connect new LV Monitor
125 |  | F16390 | Hilderthorpe Rd | N/A | 455FED | 2025-09-18 | 45918.5278 | 2025-09-18 13:03 | 45918.5437 | 0.061093 | 0.0026562 | 36 | 828 | Unplanned | 8.0 Defective Equipment | EP burnt up causing small fire
126 |  | F16389 | Ngapara area | N/A | 472FED | 2025-09-18 | 45918.6229 | 2025-09-18 15:07 | 45918.6299 | 0.067587 | 0.014093 | 191 | 916 | Unplanned | 7.0 Human error | Tripping due to OC setting at CB472, supplying CB444 and CB422 at the time
127 |  | JF014 | Ardgowan Rd | N/A | 403FED | 2025-09-19 | 45919.3562 | 2025-09-19 09:47 | 45919.4076 | 0.076441 | 0.001033 | 14 | 1036 | Planned | 11.0 Planned Shutdown | LV Monitor install
128 |  | PR501 | West Maerewhenua Rd | N/A | 421FED | 2025-09-19 | 45919.3639 | 2025-09-19 10:50 | 45919.4514 | 0.055781 | 0.00044271 | 6 | 756 | Planned | 11.0 Planned Shutdown | Trimming trees between pole 12810 and 40358
129 |  | F16502 | Weston Ngapara Rd | N/A | 428FED | 2025-09-20 | 45920.5278 | 2025-09-20 13:25 | 45920.559 | 0.16934 | 0.003763 | 51 | 2295 | Unplanned | 8.0 Defective Equipment | 11kV Jumper burnt off
130 |  | F16503 | Te Awamako Sub | N/A | 547FED | 2025-09-21 | 45921.1389 | 2025-09-21 15:33 | 45921.6479 | 0.13045 | 0.010625 | 144 | 1768 | Unplanned | 9.0 Cause Unknown | CB547 Tripped - (Nothing Found)
131 |  | F16504 | Mcleods Rd | N/A | 449FED | 2025-09-21 | 45921.1507 | 2025-09-21 12:55 | 45921.5382 | 0.32937 | 0.0033203 | 45 | 4464 | Unplanned | 2.0 Vegetation | Tree brought down 11kV Lines
132 |  | F11514 | 1119 Georgetown Pukeuri Rd | N/A | 456FED | 2025-09-21 | 45921.9556 | 2025-09-21 23:54 | 45921.9958 | 0.008559 | 0.00014757 | 2 | 116 | Unplanned | 9.0 Cause Unknown | Blown DDOs - Cause Unknown
133 |  | F16506 | Prydes Gully Rd | N/A | 421FED | 2025-09-23 | 45923.4389 | 2025-09-23 12:38 | 45923.5264 | 0.055781 | 0.00044271 | 6 | 756 | Unplanned | 8.0 Defective Equipment | Replace Pole 11136 - Unplanned Outage
134 |  | F16392 | Appleby St | N/A | 480FED | 2025-09-24 | 45924.5347 | 2025-09-24 17:12 | 45924.7167 | 1.8964 | 0.04523 | 613 | 25702 | Unplanned | 8.0 Defective Equipment | Wire off insulator causing Crossarm failure
135 |  | F16393 | Ohau Feeder | N/A | 490FED | 2025-09-25 | 45925.8083 | 2025-09-25 19:50 | 45925.8264 | 0.24747 | 0.0095182 | 129 | 3354 | Unplanned | 9.0 Cause Unknown | CB490 Tripped. Phase to phase fault - Manual Reclose Successful, cause unknown
136 |  | F12425 | 527 Burnside Rd | N/A | 449FED | 2025-09-28 | 45928.4611 | 2025-09-28 12:10 | 45928.5069 | 0.014609 | 0.00022135 | 3 | 198 | Unplanned | 9.0 Cause Unknown | Blown DDOs - Cause Unknown - Suspect Rat
137 |  | JF020 | Wainakarua Rd | N/A | 479FED | 2025-09-29 | 45929.3542 | 2025-09-29 10:37 | 45929.4424 | 0.046853 | 0.00036892 | 5 | 635 | Planned | 11.0 Planned Shutdown | LV Monitor install
138 |  | PR507 | Takaro Park RMU | N/A | 405FED | 2025-09-29 | 45929.8028 | 2025-09-30 00:30 | 45930.0208 | 0.023168 | 7.3784e-05 | 1 | 314 | Planned | 11.0 Planned Shutdown | Maintenance on RMU
139 |  | F12781 | CB432 Pukeuri | N/A | 432FED | 2025-09-30 | 45930.7264 | 2025-09-30 17:53 | 45930.7451 | 0.26843 | 0.010108 | 137 | 3638 | Unplanned | 9.0 Cause Unknown | CB432 Pukeuri Tripped
140 |  | PR506 | Roundhill Rd | N/A | 428FED | 2025-10-03 | 45933.3771 | 2025-10-03 13:21 | 45933.5563 | 0.019036 | 7.3784e-05 | 1 | 258 | Planned | 11.0 Planned Shutdown | Replace Pole 70619, 70620
141 |  | F13508 | 76 Double Hill Rd | N/A | 417FED | 2025-10-06 | 45936.3104 | 2025-10-06 09:12 | 45936.3833 | 0.023242 | 0.00022135 | 3 | 315 | Unplanned | 9.0 Cause Unknown | Blown DDOs - Cause Unknown
142 |  | NJ986 | Ngapara Georgetown Rd | N/A | 422FED | 2025-10-08 | 45938.3792 | 2025-10-08 09:23 | 45938.391 | 0.0012543 | 7.3784e-05 | 1 | 17 | Planned | 11.0 Planned Shutdown | Remove Old LV Supply from Pole 34683 to 34682
143 |  | NJ987 | Ngapara Georgetown Rd | N/A | 422FED | 2025-10-08 | 45938.4049 | 2025-10-08 13:22 | 45938.5569 | 0.59788 | 0.00273 | 37 | 8103 | Planned | 11.0 Planned Shutdown | Replace 11kV Pole 16326 and install new Transformer
144 |  | PR514A | West Maerewhenua Rd | N/A | 421FED | 2025-10-09 | 45939.3569 | 2025-10-09 15:09 | 45939.6312 | 0.17487 | 0.00044271 | 6 | 2370 | Planned | 11.0 Planned Shutdown | Replace Poles and Conductor
145 |  | PR525 | Priest Rd | N/A | 489FED | 2025-10-09 | 45939.3653 | 2025-10-09 15:10 | 45939.6319 | 0.085 | 0.00022135 | 3 | 1152 | Planned | 11.0 Planned Shutdown | Maintenance Work on TX4539.5, RMU Priest Rd
146 |  | JF031 | Hayes Rd | N/A | 413FED | 2025-10-09 | 45939.416 | 2025-10-09 11:32 | 45939.4806 | 0.013724 | 0.00014757 | 2 | 186 | Planned | 11.0 Planned Shutdown | Install LV Monitor
147 |  | PR514B | West Maerewhenua Rd | N/A | 421FED | 2025-10-10 | 45940.3569 | 2025-10-10 15:09 | 45940.6312 | 0.14299 | 0.00044271 | 6 | 1938 | Planned | 11.0 Planned Shutdown | Replace Poles and Conductor
148 |  | JF024 | Omarama Otematata Rd | N/A | 424FED | 2025-10-10 | 45940.4535 | 2025-10-10 12:44 | 45940.5306 | 0.13104 | 0.0011806 | 16 | 1776 | Planned | 11.0 Planned Shutdown | Install Stays at Pole 29648
149 |  | F16557 | Prydes Gully Rd | N/A | 413FED | 2025-10-10 | 45940.9333 | 2025-10-11 13:26 | 45941.5597 | 0.67712 | 0.0065668 | 89 | 9177 | Unplanned | 2.0 Vegetation | Tree Threw Line
150 |  | F16558 | 250 Haka Valley Rd | N/A | 413FED | 2025-10-13 | 45943.4424 | 2025-10-13 12:17 | 45943.5118 | 0.059028 | 0.00059028 | 8 | 800 | Unplanned | 8.0 Defective Equipment | Broken DDO
151 |  | PR522 | Kurow Duntroon Rd | N/A | 494FED | 2025-10-14 | 45944.3681 | 2025-10-14 15:19 | 45944.6382 | 0.22962 | 0.00059028 | 8 | 3112 | Planned | 11.0 Planned Shutdown | Install 33kV 630Amp solid links on pole 38749
152 |  | PR520 | Kemp Rd | N/A | 480FED | 2025-10-14 | 45944.4181 | 2025-10-14 15:28 | 45944.6444 | 0.12027 | 0.00036892 | 5 | 1630 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 31322 and 36965
153 |  | PR522 | Kurow Duntroon Rd | N/A | 489FED | 2025-10-15 | 45945.3722 | 2025-10-15 14:51 | 45945.6188 | 0.28813 | 0.00081163 | 11 | 3905 | Planned | 11.0 Planned Shutdown | Install 33kV 630Amp solid links on pole 38762
154 |  | NJ967 | Duntroon - Georgetown Rd | N/A | 470FED | 2025-10-15 | 45945.3993 | 2025-10-15 14:45 | 45945.6146 | 0.045746 | 0.00014757 | 2 | 620 | Planned | 11.0 Planned Shutdown | Top up oil on Tx4502.5
155 |  | F16559 | Hilderthorpe Rd | N/A | 455FED | 2025-10-15 | 45945.4042 | 2025-10-15 15:18 | 45945.6375 | 0.024792 | 7.3784e-05 | 1 | 336 | Unplanned | 8.0 Defective Equipment | Blown Transformer
156 |  | F15445 | 318 Doctors Creek Rd | N/A | 494FED | 2025-10-20 | 45950.2993 | 2025-10-20 10:22 | 45950.4319 | 0.014093 | 7.3784e-05 | 1 | 191 | Unplanned | 6.0 Wildlife | No Power - Rat found at Base of pole
157 |  | JF015 | Gemmells Crossing | N/A | 428FED | 2025-10-21 | 45951.3556 | 2025-10-21 12:14 | 45951.5097 | 0.03276 | 0.00014757 | 2 | 444 | Planned | 11.0 Planned Shutdown | Replace Pole and Arms
158 |  | JF032 | Mchenrys Rd | N/A | 413FED | 2025-10-21 | 45951.3826 | 2025-10-21 10:30 | 45951.4375 | 0.005829 | 7.3784e-05 | 1 | 79 | Planned | 11.0 Planned Shutdown | Install LV Monitor in Transformer T5227
159 |  | F16564 | Maungatiro | N/A | 413FED | 2025-10-23 | 45953.2403 | 2025-10-23 06:22 | 45953.2653 | 0.11953 | 0.0033203 | 45 | 1620 | Unplanned | 9.0 Cause Unknown | Recloser TSW1679 Locked out - Manual reclose successful
160 |  | F16566 | Buscot | N/A | 491FED | 2025-10-23 | 45953.5861 | 2025-10-23 19:06 | 45953.7958 | 0.24467 | 0.001697 | 23 | 3316 | Unplanned | 8.0 Defective Equipment | Wire down
161 |  | F16567 | Pukeuri Oamaru Rd | N/A | 432FED | 2025-10-24 | 45954.5965 | 2025-10-24 15:45 | 45954.6562 | 0.031727 | 0.00036892 | 5 | 430 | Unplanned | 2.0 Vegetation | Tree on 11kV Line at Pole 25342
162 |  | F16166 | 17 Pringles Gully Rd | N/A | 421FED | 2025-10-25 | 45955.341 | 2025-10-25 09:23 | 45955.391 | 0.0053125 | 7.3784e-05 | 1 | 72 | Unplanned | 6.0 Wildlife | No Power -Possum blew Links
163 |  | F16578 | Ohau | N/A | 490FED | 2025-10-27 | 45957.8785 | 2025-10-28 19:13 | 45958.8007 | 0.70287 | 0.0016233 | 22 | 9526 | Unplanned | 3.0 Adverse Weather | Tripping of R690, Broken Poles at Lake Ohau Station, private line
164 |  | F16664 | Big Hill | N/A | 429FED | 2025-10-27 | 45957.8792 | 2025-10-28 15:39 | 45958.6521 | 0.7391 | 0.00066406 | 9 | 10017 | Unplanned | 2.0 Vegetation | Tree across lines
165 |  | F16579 | Gards Rd | N/A | 411FED | 2025-10-28 | 45958.0021 | 2025-10-28 10:31 | 45958.4382 | 0.67461 | 0.0022135 | 30 | 9143 | Unplanned | 3.0 Adverse Weather | Snow load made Tree across lines, Pole 43402
166 |  | F16580 | Corbett Rd | N/A | 478FED | 2025-10-28 | 45958.2618 | 2025-10-28 10:34 | 45958.4403 | 1.0638 | 0.019036 | 258 | 14418 | Unplanned | 8.0 Defective Equipment | Blown Surge Arrestors fault at pole 70449
167 |  | F16576 | Ohau | N/A | 490FED | 2025-10-28 | 45958.4854 | 2025-10-28 17:05 | 45958.7118 | 1.3164 | 0.01638 | 222 | 17841 | Unplanned | 3.0 Adverse Weather | CB490 tripped, snow
168 |  | F16964 | 368 Steward Rd | N/A | 478FED | 2025-10-30 | 45960.3458 | 2025-10-30 09:32 | 45960.3972 | 0.01092 | 0.00014757 | 2 | 148 | Unplanned | 6.0 Wildlife | No Power - Possum
169 |  | PR536 | Wainakarua Rd | N/A | 479FED | 2025-10-30 | 45960.3847 | 2025-10-30 11:16 | 45960.4694 | 0.10802 | 0.00088541 | 12 | 1464 | Planned | 11.0 Planned Shutdown | Urgent replacement of Pole 13806
170 |  | F17067 | Murray Rd | N/A | 432FED | 2025-10-31 | 45961.0819 | 2025-10-31 03:11 | 45961.1326 | 0.04309 | 0.00059028 | 8 | 584 | Unplanned | 6.0 Wildlife | No Power - Possum
171 |  | PR533 | Old Slip Rd | N/A | 412FED | 2025-11-03 | 45964.3917 | 2025-11-03 12:32 | 45964.5222 | 0.013871 | 7.3784e-05 | 1 | 188 | Planned | 11.0 Planned Shutdown | Replace DDOs and Remove LAs at Pole 75285, Restrain Conductor between Pole 34742-75285
172 |  | JF036 | Parks Rd | N/A | 483FED | 2025-11-04 | 45965.3583 | 2025-11-04 12:23 | 45965.516 | 0.050247 | 0.00022135 | 3 | 681 | Planned | 11.0 Planned Shutdown | Replacing Pole 72676
173 |  | F17937 | 33kV Line Enfield Ngapara | N/A | 308FED | 2025-11-06 | 45967.3069 | 2025-11-06 08:14 | 45967.3431 | 0.70582 | 0.026341 | 357 | 9566 | Unplanned | 6.0 Wildlife | Magpie Tripped 33kV Line @ Pole 815511
174 |  | PR538A | 11kV Line Kauru Hill | N/A | 415FED | 2025-11-10 | 45971.3681 | 2025-11-10 15:54 | 45971.6625 | 0.51059 | 0.0012543 | 17 | 6920 | Planned | 11.0 Planned Shutdown | Replacing Poles, Replacing Conductor between Pole 25653-25685
175 |  | PR538B | 11kV Line Kauru Hill | N/A | 415FED | 2025-11-11 | 45972.3833 | 2025-11-11 15:29 | 45972.6451 | 0.45872 | 0.0012543 | 17 | 6217 | Planned | 11.0 Planned Shutdown | Replacing Poles, Replacing Conductor between Pole 25653-25685
176 |  | JF040 | 11kV Tenby St | N/A | 480FED | 2025-11-13 | 45974.409 | 2025-11-13 14:48 | 45974.6167 | 0.33092 | 0.0011068 | 15 | 4485 | Planned | 11.0 Planned Shutdown | Installing New Pole and Relocating Transformer from Pole 39972
177 |  | JF043 JF044 | Tenby St Moeraki | N/A | 480FED | 2025-11-14 | 45975.341 | 2025-11-14 10:40 | 45975.4444 | 0.22947 | 0.0028038 | 38 | 3110 | Planned | 11.0 Planned Shutdown | Outage to Replace DDOs Pole 19009 and Install LV Monitor
178 |  | 16592 | Caroline St | N/A | 427FED | 2025-11-14 | 45975.5847 | 2025-11-14 14:22 | 45975.5986 | 0.0029514 | 0.00014757 | 2 | 40 | Planned | 11.0 Planned Shutdown | New Conneciton
179 |  | F16509 | Katiki Area | N/A | 480FED | 2025-11-15 | 45976.0903 | 2025-11-15 03:11 | 45976.1326 | 0.17767 | 0.0053125 | 72 | 2408 | Unplanned | 9.0 Cause Unknown | S624 Tripped
180 |  | F16508 | Rocklands Rd | N/A | 416FED | 2025-11-15 | 45976.4556 | 2025-11-15 13:17 | 45976.5535 | 0.062422 | 0.00044271 | 6 | 846 | Unplanned | 5.0 Third party Interference | Car vs Pole 34445
181 |  | JF047 | MacDonalds Rd | N/A | 478FED | 2025-11-18 | 45979.3708 | 2025-11-18 13:20 | 45979.5556 | 0.05888 | 0.00022135 | 3 | 798 | Planned | 11.0 Planned Shutdown | Replace 11kV strain insulator and other maintenance
182 |  | MF542 | Maheno Herbert Rd | N/A | 417FED | 2025-11-19 | 45980.3722 | 2025-11-19 14:22 | 45980.5986 | 0.072161 | 0.00022135 | 3 | 978 | Planned | 11.0 Planned Shutdown | Replace Pole 72610
183 |  | F5917 | Wainakarua Rd | N/A | 479FED | 2025-11-19 | 45980.6354 | 2025-11-19 16:51 | 45980.7021 | 0.17 | 0.0017708 | 24 | 2304 | Unplanned | 8.0 Defective Equipment | Replace defective insulators on Pole 13738
184 |  | JF049 | Duntroon - Georgetown Rd | N/A | 444FED | 2025-11-20 | 45981.375 | 2025-11-20 11:52 | 45981.4944 | 0.038073 | 0.00022135 | 3 | 516 | Planned | 11.0 Planned Shutdown | New 11kV Underground connection
185 |  | PR544 | 11kV Island Stream Rd | N/A | 415FED | 2025-11-20 | 45981.4167 | 2025-11-20 13:33 | 45981.5646 | 0.58149 | 0.00273 | 37 | 7881 | Planned | 11.0 Planned Shutdown | Felling Trees
186 |  | F20136 | 34 Ridge Rd | N/A | 456FED | 2025-11-21 | 45982.2403 | 2025-11-21 06:41 | 45982.2785 | 0.012174 | 0.00022135 | 3 | 165 | Unplanned | 6.0 Wildlife | Blown 11kV Links Pole 42161 (rat)
187 |  | F5920 | Ridge Rd | N/A | 449FED | 2025-11-21 | 45982.6035 | 2025-11-21 15:11 | 45982.6326 | 0.012396 | 0.00029514 | 4 | 168 | Unplanned | 8.0 Defective Equipment | Replacing Crossarm @ Pole 29825
188 |  | NJ1010 & PI247 | Otematata Kurow Rd | N/A | 464FED | 2025-11-24 | 45985.3924 | 2025-11-24 11:25 | 45985.4757 | 0.2125 | 0.0017708 | 24 | 2880 | Planned | 11.0 Planned Shutdown | 33kV & 11kV Tightening
189 |  | JF055 | Waianakarua Rd | N/A | 479FED | 2025-11-27 | 45988.3757 | 2025-11-27 13:44 | 45988.5722 | 0.25057 | 0.00088541 | 12 | 3396 | Planned | 11.0 Planned Shutdown | Replace Pole 36916
190 |  | MF544 | Settlement Rd | N/A | 470FED | 2025-11-27 | 45988.3778 | 2025-11-27 11:12 | 45988.4667 | 0.0094444 | 7.3784e-05 | 1 | 128 | Planned | 11.0 Planned Shutdown | Level Transformer T4126.1
191 |  | JF054 | Saleyards Rd | N/A | 408FED | 2025-11-27 | 45988.3861 | 2025-11-27 11:23 | 45988.4743 | 0.053125 | 0.00066406 | 9 | 720 | Planned | 11.0 Planned Shutdown | Install LV Monitor
192 |  | F16600 | Weston Enfield Rd | N/A | 451FED | 2025-11-27 | 45988.6194 | 2025-11-27 18:41 | 45988.7785 | 0.25633 | 0.0045008 | 61 | 3474 | Unplanned | 2.0 Vegetation | Tree through 11kV Line
193 |  | F16598 | Glensettlement Rd | N/A | 422FED | 2025-11-27 | 45988.6646 | 2025-11-27 17:45 | 45988.7396 | 0.18018 | 0.0059028 | 80 | 2442 | Unplanned | 2.0 Vegetation | Tree Branch in 11kV Line @ Pole 12025
194 |  | F16602 | Brookstead Rd | N/A | 444FED | 2025-11-27 | 45988.675 | 2025-11-27 19:51 | 45988.8271 | 0.46646 | 0.0056814 | 77 | 6322 | Unplanned | 2.0 Vegetation | Tree Through 11kV Line Pole 36913
195 |  | F16603 | CB432 Pukeuri | N/A | 432FED | 2025-11-27 | 45988.6903 | 2025-11-27 18:04 | 45988.7528 | 0.59721 | 0.010182 | 138 | 8094 | Unplanned | 9.0 Cause Unknown | CB432 Pukeuri Tripped
196 |  | F18333B | 164 Post Office Gully | N/A | 486FED | 2025-11-27 | 45988.716 | 2025-11-27 17:36 | 45988.7333 | 0.1244 | 0.0068619 | 93 | 1686 | Unplanned | 8.0 Defective Equipment | 11kV Wires down between Pole 18333 and 72166
197 |  | JF048 | Ashlands Rd | N/A | 480FED | 2025-11-28 | 45989.3819 | 2025-11-28 13:50 | 45989.5764 | 0.041319 | 0.00014757 | 2 | 560 | Planned | 11.0 Planned Shutdown | New Transformer install at pole 30404
198 |  | F16605 | Towey St | N/A | 409FED | 2025-12-01 | 45992.0431 | 2025-12-01 03:34 | 45992.1486 | 9.0139 | 0.080425 | 1090 | 122165 | Unplanned | 9.0 Cause Unknown | Blown 11KV Jumper Pole 36454
199 |  | PR553 | Kaik Rd | N/A | 478FED | 2025-12-02 | 45993.3597 | 2025-12-02 10:49 | 45993.4507 | 0.31897 | 0.0024349 | 33 | 4323 | Planned | 11.0 Planned Shutdown | Replace Transformer T2854
200 |  | 16609 | Cormacks Kia Ora Rd | N/A | 428FED | 2025-12-02 | 45993.4299 | 2025-12-02 12:28 | 45993.5194 | 0.3141 | 0.0024349 | 33 | 4257 | Unplanned | 8.0 Defective Equipment | Replace ABS1418 Cormacks
201 |  | MF543 | Cormacks Kia Ora Rd | N/A | 428FED | 2025-12-02 | 45993.5139 | 2025-12-02 14:44 | 45993.6139 | 0.2975 | 0.002066 | 28 | 4032 | Planned | 11.0 Planned Shutdown | Replace 11kV Pole 43050 and crossarm on pole 28894
202 |  | F22106 | 137 Settlement Rd | N/A | 479FED | 2025-12-03 | 45994.2799 | 2025-12-03 07:49 | 45994.3257 | 0.0048698 | 7.3784e-05 | 1 | 66 | Unplanned | 6.0 Wildlife | Blown 11kV Links Pole 30063 - Possum
203 |  | F22109 | 21 Hillies Rd, Kurow | N/A | 411FED | 2025-12-03 | 45994.3118 | 2025-12-03 09:54 | 45994.4125 | 0.08559 | 0.00059028 | 8 | 1160 | Unplanned | 6.0 Wildlife | Blown 11kV Links Pole 27101 - Dead Bird
204 |  | PR551 | Cosy Dell Rd | N/A | 479FED | 2025-12-03 | 45994.3799 | 2025-12-03 14:14 | 45994.5931 | 0.6116 | 0.0019922 | 27 | 8289 | Planned | 11.0 Planned Shutdown | Fell Trees between Pole 39500 and Pole 10333
205 |  | NJ1017 PI248 | Lake Ohau Rd | N/A | 490FED | 2025-12-04 | 45995.3424 | 2025-12-04 16:22 | 45995.6819 | 2.1969 | 0.0075998 | 103 | 29775 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor
206 |  | JF056 | Oakleigh Crescent | N/A | 437FED | 2025-12-05 | 45996.3639 | 2025-12-05 11:25 | 45996.4757 | 0.4039 | 0.0025087 | 34 | 5474 | Planned | 11.0 Planned Shutdown | Install LV Monitor
207 |  | F16610 | Twizel Omarama Rd | N/A | 492FED | 2025-12-05 | 45996.8069 | 2025-12-05 19:30 | 45996.8125 | 0.006493 | 0.00081163 | 11 | 88 | Unplanned | 3.0 Adverse Weather | Silage Wrap in Power Lines at Pole 21095
208 |  | F16611-1 | R690 Freehold Creek | N/A | 490FED | 2025-12-05 | 45996.8076 | 2025-12-05 19:30 | 45996.8125 | 0.011363 | 0.0016233 | 22 | 154 | Unplanned | 9.0 Cause Unknown | R690 Freehold Creek Tripped
209 |  | NJ1021A | Lake Ohau Rd | N/A | 490FED | 2025-12-08 | 45999.3688 | 2025-12-08 15:56 | 45999.6639 | 0.27027 | 0.00066406 | 9 | 3663 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor
210 |  | NJ1022 | Lake Ohau Rd | N/A | 490FED | 2025-12-09 | 46000.3382 | 2025-12-09 17:05 | 46000.7118 | 0.9527 | 0.0017708 | 24 | 12912 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor
211 |  | JF057 | Hardacre Place | N/A | 423FED | 2025-12-09 | 46000.3611 | 2025-12-09 09:39 | 46000.4021 | 0.060946 | 0.001033 | 14 | 826 | Planned | 11.0 Planned Shutdown | Install LV Monitor
212 |  | F16613 | The Dasher Rd | N/A | 483FED | 2025-12-09 | 46000.5847 | 2025-12-09 14:43 | 46000.6132 | 0.018151 | 0.00044271 | 6 | 246 | Unplanned | 8.0 Defective Equipment | 11kV Wire floating at Pole 30937
213 |  | NJ1021B | Lake Ohau Rd | N/A | 490FED | 2025-12-10 | 46001.3549 | 2025-12-10 15:47 | 46001.6576 | 0.28658 | 0.00066406 | 9 | 3884 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor
214 |  | JF046 | Omarama Otematata Rd | N/A | 425FED | 2025-12-10 | 46001.5424 | 2025-12-10 13:45 | 46001.5729 | 0.022726 | 0.00051649 | 7 | 308 | Planned | 11.0 Planned Shutdown | Install LV Monitor
215 |  | NJ1021C | Lake Ohau Rd | N/A | 490FED | 2025-12-11 | 46002.3549 | 2025-12-11 15:55 | 46002.6632 | 0.29189 | 0.00066406 | 9 | 3956 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor
216 |  | NJ1021D | Lake Ohau Rd | N/A | 490FED | 2025-12-12 | 46003.3542 | 2025-12-12 13:01 | 46003.5424 | 0.17229 | 0.00066406 | 9 | 2335 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor
217 |  | NJ1023 | Lake Ohau Rd | N/A | 490FED | 2025-12-15 | 46006.3646 | 2025-12-15 15:25 | 46006.6424 | 0.6493 | 0.0016233 | 22 | 8800 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor
218 |  | PR546 | Hillgrove Moeraki Rd | N/A | 480FED | 2025-12-15 | 46006.4194 | 2025-12-15 15:32 | 46006.6472 | 0.024201 | 7.3784e-05 | 1 | 328 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 27550 and 70403
219 |  | NJ1021E | Lake Ohau Rd | N/A | 490FED | 2025-12-16 | 46007.3542 | 2025-12-16 15:36 | 46007.65 | 0.27876 | 0.00066406 | 9 | 3778 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor
220 |  | JF064 | Slaughter Yard Rd | N/A | 451FED | 2025-12-16 | 46007.3549 | 2025-12-17 12:14 | 46008.5097 | 0.016454 | 7.3784e-05 | 1 | 223 | Planned | 11.0 Planned Shutdown | Replacing Poles 70369 and 75175
221 |  | JF066 | Oamaru Alma Rd | N/A | 427FED | 2025-12-16 | 46007.3639 | 2025-12-16 10:39 | 46007.4437 | 0.042426 | 0.00036892 | 5 | 575 | Planned | 11.0 Planned Shutdown | Connection upgrades
222 |  | F16620A & B | Woodburn Rd | N/A | 417FED | 2025-12-16 | 46007.5917 | 2025-12-16 19:30 | 46007.8125 | 1.6094 | 0.018815 | 255 | 21812 | Unplanned | 1.0 Lightning | Replacing ABS1078 with 11kV Links & DDOs at pole 34517 due to lightning strike
223 |  | F11233 | Main Rd Maheno | N/A | 414FED | 2025-12-16 | 46007.6021 | 2025-12-16 17:37 | 46007.734 | 0.30104 | 0.0098133 | 133 | 4080 | Unplanned | 1.0 Lightning | Lightning Blew Transformer at Pole 19073
224 |  | NJ1021F | Lake Ohau Rd | N/A | 490FED | 2025-12-17 | 46008.3542 | 2025-12-17 16:57 | 46008.7063 | 0.32428 | 0.00066406 | 9 | 4395 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor
225 |  | NJ1032 | Ben Omar Rd | N/A | 424FED | 2025-12-17 | 46008.391 | 2025-12-17 14:37 | 46008.609 | 0.046337 | 0.00014757 | 2 | 628 | Planned | 11.0 Planned Shutdown | Replace Pole 71690 and install new DDOs and Transformer
226 |  | MF545 | Waimotu Rd | N/A | 415FED | 2025-12-18 | 46009.3757 | 2025-12-18 10:39 | 46009.4437 | 0.028923 | 0.00029514 | 4 | 392 | Planned | 11.0 Planned Shutdown | Install New Transformer Fusing 3 x 160a fuse carriers
227 |  | NJ1031 | Mcleod Rd | N/A | 449FED | 2025-12-18 | 46009.3847 | 2025-12-18 12:51 | 46009.5354 | 0.080056 | 0.00036892 | 5 | 1085 | Planned | 11.0 Planned Shutdown | Replacing Pole 24864 and Tighten Hardware at Pole 40177
228 |  | F24825 | Ross Rd | N/A | 479FED | 2025-12-19 | 46010.6944 | 2025-12-19 17:28 | 46010.7278 | 0.0035417 | 7.3784e-05 | 1 | 48 | Unplanned | 6.0 Wildlife | Blown HV Fuses - Rats
229 |  | F16625 | Robins Rd | N/A | 416FED | 2025-12-22 | 46013.8187 | 2025-12-23 00:38 | 46014.0264 | 3.3486 | 0.045525 | 617 | 45384 | Unplanned | 5.0 Third party Interference | Car vs Pole 28804 and 28805
230 |  | F33884 | Battersby Rd | N/A | 449FED | 2025-12-24 | 46015.6125 | 2025-12-24 15:55 | 46015.6632 | 0.0053863 | 7.3784e-05 | 1 | 73 | Unplanned | 9.0 Cause Unknown | Replace Pole 33884 - Damaged
231 |  | F26926 | 1686 Weston Ngapara Rd | N/A | 420FED | 2025-12-30 | 46021.4118 | 2025-12-30 10:30 | 46021.4375 | 0.00273 | 7.3784e-05 | 1 | 37 | Unplanned | 9.0 Cause Unknown | Blown HV Fuses - Cause Unknown (Probably a rat)
232 |  | NJ1029 | Omarama Otematata Rd | N/A | 411FED | 2026-01-06 | 46028.4597 | 2026-01-06 11:36 | 46028.4833 | 0.052682 | 0.0015495 | 21 | 714 | Planned | 11.0 Planned Shutdown | Install LV Monitor
233 |  | PR571 | Settlement Rd | N/A | 424FED | 2026-01-06 | 46028.641 | 2026-01-06 15:23 | 46028.641 | 0.071497 | 0.00022135 | 3 | 969 | Planned | 11.0 Planned Shutdown | Trimming Trees Pole 71607 and 71608
234 |  | F16628 | Prydes Gully Rd | N/A | 421FED | 2026-01-07 | 46029.7292 | 2026-01-07 18:41 | 46029.7785 | 0.44344 | 0.0066406 | 90 | 6010 | Unplanned | 1.0 Lightning | Lightning Strike - Blown LA Pole 40217
235 |  | F16630 | Kurow | N/A | 411FED | 2026-01-07 | 46029.7896 | 2026-01-07 19:14 | 46029.8014 | 0.46322 | 0.030104 | 408 | 6278 | Unplanned | 1.0 Lightning | CB411 Tripping (Lightning Storm)
236 |  | F16632 | Kurow | N/A | 411FED | 2026-01-09 | 46031.0049 | 2026-01-09 14:16 | 46031.5944 | 0.45348 | 0.030178 | 409 | 6146 | Unplanned | 8.0 Defective Equipment | CB411 Tripping (Blown LA)
237 |  | F16511 | Gards Rd | N/A | 411FED | 2026-01-10 | 46032.8847 | 2026-01-10 22:20 | 46032.9306 | 0.25559 | 0.0022135 | 30 | 3464 | Unplanned | 2.0 Vegetation | Branch on 11kV Line between Pole 32758 and Pole 32759
238 |  | F16513 | Shag Point | N/A | 480FED | 2026-01-11 | 46033.4132 | 2026-01-11 12:40 | 46033.5278 | 0.19479 | 0.0011806 | 16 | 2640 | Unplanned | 8.0 Defective Equipment | Disconnected 11kV Ampact at Pole 39276
239 |  | F16514 | CB432 Pukeuri | N/A | 432FED | 2026-01-11 | 46033.5854 | 2026-01-11 16:00 | 46033.6667 | 0.71246 | 0.013281 | 180 | 9656 | Unplanned | 9.0 Cause Unknown | CB432 Pukeuri Tripped
240 |  | F29292 | 1063 Coal Pit Rd | N/A | 429FED | 2026-01-12 | 46034.3861 | 2026-01-12 11:28 | 46034.4778 | 0.058437 | 0.00044271 | 6 | 792 | Unplanned | 9.0 Cause Unknown | Blown 11kV Link Pole 15893
241 |  | F29363 | 26 West Maerewhenua Rd | N/A | 421FED | 2026-01-12 | 46034.7014 | 2026-01-12 17:08 | 46034.7139 | 0.0079687 | 0.00044271 | 6 | 108 | Unplanned | 8.0 Defective Equipment | 11kV Crossarm Twisted at Pole 12805
242 |  | JF067 | Joy Street | N/A | 403FED | 2026-01-14 | 46036.3646 | 2026-01-14 10:40 | 46036.4444 | 0.033941 | 0.00029514 | 4 | 460 | Planned | 11.0 Planned Shutdown | Install LV Monitor
243 |  | MF548 | Rooneys Rd | N/A | 430FED | 2026-01-16 | 46038.359 | 2026-01-16 15:27 | 46038.6438 | 0.12101 | 0.00029514 | 4 | 1640 | Planned | 11.0 Planned Shutdown | Replace Pole 28124 & Transformer & Connect New LV Cable
244 |  | F30300 | 233 Gards Rd | N/A | 411FED | 2026-01-18 | 46040.4431 | 2026-01-18 11:55 | 46040.4965 | 0.0056814 | 7.3784e-05 | 1 | 77 | Unplanned | 6.0 Wildlife | Blown HV fuses - Rat
245 |  | F16635 | Kakanui Bridge | N/A | 416FED | 2026-01-19 | 46041.6417 | 2026-01-19 16:20 | 46041.6806 | 0.2975 | 0.0053125 | 72 | 4032 | Unplanned | 8.0 Defective Equipment | Jumper burnt off at Pole 18371
246 |  | JF070 | Coronet Place | N/A | 426FED | 2026-01-22 | 46044.4472 | 2026-01-22 12:45 | 46044.5312 | 0.11606 | 0.0009592 | 13 | 1573 | Planned | 11.0 Planned Shutdown | Install LV Monitor
247 |  | NJ1049 | Kakanui Valley Rd | N/A | 415FED | 2026-01-23 | 46045.3806 | 2026-01-23 10:01 | 46045.4174 | 0.011732 | 0.00022135 | 3 | 159 | Planned | 11.0 Planned Shutdown | Raise and terminate new cable
248 |  | F16545 | Doctors Creek Rd | N/A | 411FED | 2026-01-25 | 46047.2646 | 2026-01-25 09:20 | 46047.3889 | 0.14587 | 0.0022135 | 30 | 1977 | Unplanned | 2.0 Vegetation | Tree Through 11kV spur near pole 70884
249 |  | NJ1052 | TY Duncan Rd | N/A | 432FED | 2026-01-27 | 46049.3792 | 2026-01-27 13:52 | 46049.5778 | 0.021102 | 7.3784e-05 | 1 | 286 | Planned | 11.0 Planned Shutdown | Oil Top up TX3073
250 |  | PR561 | Kauru hill Rd | N/A | 415FED | 2026-01-29 | 46051.3785 | 2026-01-29 15:27 | 46051.6438 | 0.46145 | 0.0012543 | 17 | 6254 | Planned | 11.0 Planned Shutdown | Replacing Conductor between Pole 24653 and Pole 25685
251 |  | F31827 | 59 Whitstone Five Forks Rd | N/A | 451FED | 2026-01-29 | 46051.6347 | 2026-01-29 19:07 | 46051.7965 | 0.051575 | 0.00022135 | 3 | 699 | Unplanned | 2.0 Vegetation | Tree across 11kV Line @ Pole 487618
252 |  | NJ047 | Otematata Station | N/A | 425FED | 2026-01-30 | 46052.375 | 2026-01-30 13:28 | 46052.5611 | 0.27219 | 0.001033 | 14 | 3689 | Planned | 11.0 Planned Shutdown | Installing New Pole North of Pole 71742 with 11kV Links
253 |  | F CB451 | Enfield Sub | N/A | 451FED | 2026-01-31 | 46053.4854 | 2026-01-31 12:42 | 46053.5292 | 0.22563 | 0.0044271 | 60 | 3058 | Unplanned | 9.0 Cause Unknown | CB451 tripped - Nothing found
254 |  | F16653 | Mckerrow Rd | N/A | 479FED | 2026-02-02 | 46055.3889 | 2026-02-02 15:27 | 46055.6438 | 0.1061 | 0.00029514 | 4 | 1438 | Unplanned | 8.0 Defective Equipment | Replacing Pole 72134
255 |  | JF075 | Install LV Monitor | N/A | 473FED | 2026-02-02 | 46055.4194 | 2026-02-02 11:20 | 46055.4722 | 0.0056076 | 7.3784e-05 | 1 | 76 | Planned | 11.0 Planned Shutdown | Install LV Monitor
256 |  | JF077 | Smillies Rd | N/A | 472FED | 2026-02-04 | 46057.4 | 2026-02-04 10:48 | 46057.45 | 0.0053125 | 7.3784e-05 | 1 | 72 | Planned | 11.0 Planned Shutdown | Install LV Monitor
257 |  | NJ1053 | 11kV Line Priest Rd | N/A | 489FED | 2026-02-05 | 46058.3646 | 2026-02-05 13:56 | 46058.5806 | 0.068841 | 0.00022135 | 3 | 933 | Planned | 11.0 Planned Shutdown | Level Transformer T4539
258 |  | JF076 | Livingstone Duntroon Rd | N/A | 496FED | 2026-02-05 | 46058.4076 | 2026-02-05 11:21 | 46058.4729 | 0.013871 | 0.00014757 | 2 | 188 | Planned | 11.0 Planned Shutdown | Install LV Monitor
259 |  | F16633 | 912 Twizel Omarama Rd | N/A | 491FED | 2026-02-05 | 46058.4319 | 2026-02-05 11:26 | 46058.4764 | 0.014167 | 0.00022135 | 3 | 192 | Unplanned | 8.0 Defective Equipment | Tighten and replace nuts on Poles 43163 and 43158
260 |  | F16656 | Omarama Sub | N/A | 510FED | 2026-02-05 | 46058.7972 | 2026-02-05 19:22 | 46058.8069 | 0.50513 | 0.036081 | 489 | 6846 | Unplanned | 9.0 Cause Unknown | R808 Tripped
261 |  | NJ1051 | Northstar | N/A | 458FED | 2026-02-08 | 46061.5 | 2026-02-08 16:43 | 46061.6965 | 0.020881 | 7.3784e-05 | 1 | 283 | Planned | 11.0 Planned Shutdown | RMU Maintenance
262 |  | PR578 | Waianakarua Rd | N/A | 479FED | 2026-02-09 | 46062.4021 | 2026-02-09 13:36 | 46062.5667 | 0.017487 | 7.3784e-05 | 1 | 237 | Planned | 11.0 Planned Shutdown | Replace Cable termination on Pole 71150
263 |  | JF080 | Coal Pit Rd | N/A | 429FED | 2026-02-10 | 46063.3521 | 2026-02-10 12:25 | 46063.5174 | 0.15805 | 0.00066406 | 9 | 2142 | Planned | 11.0 Planned Shutdown | Replace Poles 41444 and 41121
264 |  | JF082 | SH83 | N/A | 492FED | 2026-02-10 | 46063.4444 | 2026-02-10 11:29 | 46063.4785 | 0.0036154 | 7.3784e-05 | 1 | 49 | Planned | 11.0 Planned Shutdown | ABS1429 Maintenance
265 |  | NJ1066 | Maheno Kakanui Rd | N/A | 416FED | 2026-02-12 | 46065.3569 | 2026-02-12 12:07 | 46065.5049 | 0.031432 | 0.00014757 | 2 | 426 | Planned | 11.0 Planned Shutdown | Replace DDOs and Las on Pole 30614
266 |  | PR579A | Old Slip Rd | N/A | 412FED | 2026-02-12 | 46065.3771 | 2026-02-12 14:52 | 46065.6194 | 0.025751 | 7.3784e-05 | 1 | 349 | Planned | 11.0 Planned Shutdown | Fibre Install
267 |  | NJ1060 | Otematata | N/A | 425FED | 2026-02-12 | 46065.3812 | 2026-02-12 15:19 | 46065.6382 | 0.4095 | 0.0011068 | 15 | 5550 | Planned | 11.0 Planned Shutdown | Install new NOJA Recloser
268 |  | NJ1036 | Fuschia Creek Rd | N/A | 483FED | 2026-02-13 | 46066.3639 | 2026-02-13 15:36 | 46066.65 | 0.1216 | 0.00029514 | 4 | 1648 | Planned | 11.0 Planned Shutdown | Replace LV Pole 30984P and Replace Transformer
269 |  | PR579B | Old Slip Rd | N/A | 412FED | 2026-02-13 | 46066.491 | 2026-02-13 14:05 | 46066.5868 | 0.010182 | 7.3784e-05 | 1 | 138 | Planned | 11.0 Planned Shutdown | Tree Fault
270 |  | F10321 | Glencoe Rd | N/A | 479FED | 2026-02-14 | 46067.7521 | 2026-02-14 18:37 | 46067.7757 | 0.10536 | 0.0030989 | 42 | 1428 | Unplanned | 8.0 Defective Equipment | Faulty connections at Pole 10321
271 |  | F29825 | Ridge Rd | N/A | 449FED | 2026-02-14 | 46067.8521 | 2026-02-14 20:53 | 46067.8701 | 0.0076736 | 0.00029514 | 4 | 104 | Unplanned | 2.0 Vegetation | Tree across line
272 |  | PR584 | Dunrobin Rd | N/A | 486FED | 2026-02-19 | 46072.3757 | 2026-02-19 12:23 | 46072.516 | 0.47252 | 0.0023611 | 32 | 6404 | Planned | 11.0 Planned Shutdown | Installing Transformer at Pole 39793
273 |  | PR586 | Oamaru Alma Rd | N/A | 427FED | 2026-02-19 | 46072.384 | 2026-02-19 11:05 | 46072.4618 | 0.0082639 | 7.3784e-05 | 1 | 112 | Planned | 11.0 Planned Shutdown | Replacing DDOs & Removing Surge Arrestors at Pole 31125
274 |  | PR587 PR588 | Oamaru Alma Rd | N/A | 427FED | 2026-02-20 | 46073.3569 | 2026-02-20 16:14 | 46073.6764 | 0.033941 | 7.3784e-05 | 1 | 460 | Planned | 11.0 Planned Shutdown | Replacing Pole 71846
275 |  | F35481 | 383 Fuschia Creek Rd | N/A | 483FED | 2026-02-22 | 46075.3139 | 2026-02-22 08:40 | 46075.3611 | 0.0050173 | 7.3784e-05 | 1 | 68 | Unplanned | 6.0 Wildlife | Blown DDOs
276 |  | F6020 | Herbert Hampden Rd | N/A | 479FED | 2026-02-23 | 46076.5465 | 2026-02-23 14:44 | 46076.6139 | 0.28628 | 0.0029514 | 40 | 3880 | Unplanned | 8.0 Defective Equipment | Replace 11kV Crossarm Pole 28399
277 |  | F35753 | 2705 Herbert Hampden Rd | N/A | 479FED | 2026-02-24 | 46077.3118 | 2026-02-24 09:26 | 46077.3931 | 0.0086328 | 7.3784e-05 | 1 | 117 | Unplanned | 6.0 Wildlife | Roden Blew 11kV Link Pole 28346
278 |  | NJ1071A | Lake Ohau Rd | N/A | 490FED | 2026-02-24 | 46077.375 | 2026-02-24 16:05 | 46077.6701 | 0.28223 | 0.00066406 | 9 | 3825 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor between Pole 41815 and 41823
279 |  | NJ1071B | Lake Ohau Rd | N/A | 490FED | 2026-02-25 | 46078.3694 | 2026-02-25 15:48 | 46078.6583 | 0.27625 | 0.00066406 | 9 | 3744 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor between Pole 41815 and 41823
280 |  | NJ1071C | Lake Ohau Rd | N/A | 490FED | 2026-02-26 | 46079.3743 | 2026-02-26 12:13 | 46079.509 | 0.12883 | 0.00066406 | 9 | 1746 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor between Pole 41815 and 41823
281 |  | F36193 | 386 Farm Rd | N/A | 413FED | 2026-02-27 | 46080.4347 | 2026-02-27 12:33 | 46080.5229 | 0.0093706 | 7.3784e-05 | 1 | 127 | Unplanned | 9.0 Cause Unknown | Blown 11kV Links at Pole 43203
282 |  | NJ1071D | Lake Ohau Rd | N/A | 490FED | 2026-03-02 | 46083.4132 | 2026-03-02 15:46 | 46083.6569 | 0.23308 | 0.00066406 | 9 | 3159 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor between Pole 41815 and 41823
283 |  | NJ1071E | Lake Ohau Rd | N/A | 490FED | 2026-03-03 | 46084.3694 | 2026-03-03 15:51 | 46084.6604 | 0.27824 | 0.00066406 | 9 | 3771 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor between Pole 41815 and 41823
284 |  | F36938 | 74 Otiake Rd | N/A | 411FED | 2026-03-03 | 46084.7986 | 2026-03-03 23:48 | 46084.9917 | 0.69741 | 0.0025087 | 34 | 9452 | Unplanned | 2.0 Vegetation | Tree through 11kV Line at Pole 827940
285 |  | NJ1071F | Lake Ohau Rd | N/A | 490FED | 2026-03-04 | 46085.3639 | 2026-03-04 14:50 | 46085.6181 | 0.24305 | 0.00066406 | 9 | 3294 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Conductor between Pole 41815 and 41823
286 |  | F37039 | 1561 Twizel Omarama Rd | N/A | 491FED | 2026-03-04 | 46085.5993 | 2026-03-04 15:54 | 46085.6625 | 0.0067144 | 7.3784e-05 | 1 | 91 | Unplanned | 6.0 Wildlife | Possom at Pole 33860 Blew 11kV Links at Pole 39772
287 |  | PR591 | Stonewall Rd | N/A | 416FED | 2026-03-05 | 46086.3597 | 2026-03-05 12:39 | 46086.5271 | 0.50129 | 0.0021397 | 29 | 6794 | Planned | 11.0 Planned Shutdown | Felling Trees between pole 124925 and pole 24929
288 |  | PI260 | Lake Ohau Rd | N/A | 490FED | 2026-03-05 | 46086.3799 | 2026-03-05 15:34 | 46086.6486 | 0.54254 | 0.0014019 | 19 | 7353 | Planned | 11.0 Planned Shutdown | Replacing Conductor between Pole 874103 and Pole 41815
289 |  | NJ1078 | Whitestone Five Forks Rd | N/A | 451FED | 2026-03-05 | 46086.4222 | 2026-03-05 10:54 | 46086.4542 | 0.0033941 | 7.3784e-05 | 1 | 46 | Planned | 11.0 Planned Shutdown | Installing 100A Carrier into SFB432495
290 |  | F37412 | 286 Hilderthorpe Rd | N/A | 455FED | 2026-03-07 | 46088.4181 | 2026-03-07 10:54 | 46088.4542 | 0.0076736 | 0.00014757 | 2 | 104 | Unplanned | 5.0 Third party Interference | Irrigation Sprayer hit Line and Blew 11kV Link
291 |  | PR594A | Hakataramea Hwy | N/A | 412FED | 2026-03-07 | 46088.4951 | 2026-03-07 14:22 | 46088.5986 | 0.51671 | 0.0034679 | 47 | 7003 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 15552 and 34987
292 |  | PR594B | Hakataramea Hwy | N/A | 412FED | 2026-03-08 | 46089.4319 | 2026-03-08 14:59 | 46089.6243 | 0.9606 | 0.0034679 | 47 | 13019 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 15552 and 34987
293 |  | F16517 | Weston Ngapara Rd | N/A | 449FED | 2026-03-08 | 46089.5701 | 2026-03-08 16:04 | 46089.6694 | 0.010551 | 7.3784e-05 | 1 | 143 | Unplanned | 5.0 Third party Interference | Replacing Pole 41428 hit by Vehicle
294 |  | F16665A | 11kV Line Tokarahi Lime Works | N/A | 421FED | 2026-03-09 | 46090.5007 | 2026-03-09 12:53 | 46090.5368 | 0.17649 | 0.0033941 | 46 | 2392 | Unplanned | 5.0 Third party Interference | Truck Brought down 11kV Line
295 |  | PR595 | Gards Rd | N/A | 411FED | 2026-03-10 | 46091.3396 | 2026-03-10 15:42 | 46091.6542 | 0.46794 | 0.001033 | 14 | 6342 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 32758 and 32759
296 |  | PR593A | Otiake Rd | N/A | 411FED | 2026-03-11 | 46092.334 | 2026-03-11 15:04 | 46092.6278 | 1.0612 | 0.0025087 | 34 | 14382 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 827940 and 40789 and new connection on Grants Rd
297 |  | PR593B | Otiake Rd | N/A | 411FED | 2026-03-12 | 46093.3479 | 2026-03-12 16:26 | 46093.6847 | 1.2167 | 0.0025087 | 34 | 16490 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 827940 and 40789 and new connection on Grants Rd
298 |  | PR598 | Haka Highway | N/A | 412FED | 2026-03-13 | 46094.3562 | 2026-03-13 13:52 | 46094.5778 | 0.047074 | 0.00014757 | 2 | 638 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 72425and 72427
299 |  | F38519 | Diggers Gully Rd | N/A | 411FED | 2026-03-15 | 46096.3854 | 2026-03-15 10:30 | 46096.4375 | 0.011068 | 0.00014757 | 2 | 150 | Unplanned | 6.0 Wildlife | Rats caused HV fuses to Blow 819504
300 |  | F38596 | Currie Rd | N/A | 414FED | 2026-03-15 | 46096.8292 | 2026-03-15 22:04 | 46096.9194 | 0.028776 | 0.00022135 | 3 | 390 | Unplanned | 6.0 Wildlife | Birds Caused HV fuses to Blow at Pole 41829
301 |  | F39534 | 2 Steward Rd | N/A | 432FED | 2026-03-22 | 46103.9806 | 2026-03-23 00:28 | 46104.0194 | 0.0041319 | 7.3784e-05 | 1 | 56 | Unplanned | 6.0 Wildlife | No Power - Blown DDO Links - Rats
302 |  | F16670 | 1 Forrest Rd | N/A | 449FED | 2026-03-26 | 46107.5847 | 2026-03-26 16:32 | 46107.6889 | 0.92754 | 0.015569 | 211 | 12571 | Unplanned | 2.0 Vegetation | Tree through 11kV Spur Line near Pole 71416 Tripped Recloser R686
303 |  | JF083 | Turnbulls Rd | N/A | 486FED | 2026-03-27 | 46108.3965 | 2026-03-27 10:29 | 46108.4368 | 0.017118 | 0.00029514 | 4 | 232 | Planned | 11.0 Planned Shutdown | Remove DDOs Las and T1803 at Pole 41413 (Decomission)
304 |  | NJ1055 | Kakanui Rd | N/A | 416FED | 2026-03-30 | 46111.3542 | 2026-03-30 16:45 | 46111.6979 | 2.5932 | 0.0052387 | 71 | 35145 | Planned | 11.0 Planned Shutdown | Kakanui Bridge Works
305 |  | JF079 | Duntroon Georgetown Rd | N/A | 470FED | 2026-03-30 | 46111.4069 | 2026-03-30 11:07 | 46111.4632 | 0.0059765 | 7.3784e-05 | 1 | 81 | Planned | 11.0 Planned Shutdown | Install LV Monitor
306 |  | NJ1056 | Kakanui Rd | N/A | 416FED | 2026-03-31 | 46112.3542 | 2026-03-31 16:47 | 46112.6993 | 2.6036 | 0.0052387 | 71 | 35287 | Planned | 11.0 Planned Shutdown | Kakanui Bridge Works
307 |  | NJ1083 | Pukeuri | N/A | 432FED | 2026-03-31 | 46112.3639 | 2026-03-31 15:05 | 46112.6285 | 0.42168 | 0.0011068 | 15 | 5715 | Planned | 11.0 Planned Shutdown | Pukeuri Substation Alterations
308 |  | ¹ Extend table as necessary to disclose information for all individual interruptions